## Data entry
AXG Data Entry
Client Name
Tag Number
Service |  |  | Error Check
AXG Model | AXG032-G |  | OK
AXG MS Suffix Code
AXG Type | General Purpose |  | OK
AXG Liner | PFA |  | OK
AXG Calibration | Standard (Code B) |  | OK
AXG Transmitter | AXG Integral or AXG4A |  | OK
Size (mm) | 32 |  |  | 25-200
Flow | 100 | l/min
| 48.2549 | 482.5486
Vmax | 2.0723 | m/sec
Span Check: | OK
| Size (mm) | ID | Area (m2) | l/sec | l/min | l/hr | m3/hr | m3/min | m3/sec | Ml/day | bbl(US_Oil)/day | bbl(US_Beer)/day
| 2.5 | 2.5 | 4.9087e-06 | 0.0049087 | 0.29452 | 17.6715 | 0.017671 | 0.00029452 | 4.9087e-06 | 0.00042412 | 2.6676 | 3.6142
| 5 | 5 | 1.9635e-05 | 0.019635 | 1.1781 | 70.6858 | 0.070686 | 0.0011781 | 1.9635e-05 | 0.0016965 | 10.6704 | 14.4567
| 10 | 10 | 7.854e-05 | 0.07854 | 4.7124 | 282.7433 | 0.28274 | 0.0047124 | 7.854e-05 | 0.0067858 | 42.6817 | 57.8268
| 15 | 15 | 0.00017671 | 0.17671 | 10.6029 | 636.1725 | 0.63617 | 0.010603 | 0.00017671 | 0.015268 | 96.0337 | 130.1102
| 25 | 25 | 0.00049087 | 0.49087 | 29.4524 | 1767.1459 | 1.7671 | 0.029452 | 0.00049087 | 0.042412 | 266.7603 | 361.4172
| 32 | 32 | 0.00080425 | 0.80425 | 48.2549 | 2895.2918 | 2.8953 | 0.048255 | 0.00080425 | 0.069487 | 437.0601 | 592.146
| 40 | 40 | 0.0012566 | 1.2566 | 75.3982 | 4523.8934 | 4.5239 | 0.075398 | 0.0012566 | 0.10857 | 682.9064 | 925.2281
| 50 | 50 | 0.0019635 | 1.9635 | 117.8097 | 7068.5835 | 7.0686 | 0.11781 | 0.0019635 | 0.16965 | 1067.0413 | 1445.669
| 65 | 65 | 0.0033183 | 3.3183 | 199.0984 | 11945.9061 | 11.9459 | 0.1991 | 0.0033183 | 0.2867 | 1803.2998 | 2443.1805
| 80 | 80 | 0.0050265 | 5.0265 | 301.5929 | 18095.5737 | 18.0956 | 0.30159 | 0.0050265 | 0.43429 | 2731.6257 | 3700.9125
| 100 | 100 | 0.007854 | 7.854 | 471.2389 | 28274.3339 | 28.2743 | 0.47124 | 0.007854 | 0.67858 | 4268.1652 | 5782.6758
| 125 | 125 | 0.012272 | 12.2718 | 736.3108 | 44178.6467 | 44.1786 | 0.73631 | 0.012272 | 1.0603 | 6669.0081 | 9035.431
| 150 | 150 | 0.017671 | 17.6715 | 1060.2875 | 63617.2512 | 63.6173 | 1.0603 | 0.017671 | 1.5268 | 9603.3717 | 13011.0206
| 200 | 200 | 0.031416 | 31.4159 | 1884.9556 | 113097.3355 | 113.0973 | 1.885 | 0.031416 | 2.7143 | 17072.6608 | 23130.7033
| 250 | 250 | 0.049087 | 49.0874 | 2945.2431 | 176714.5868 | 176.7146 | 2.9452 | 0.049087 | 4.2412 | 26676.0324 | 36141.7238
| 300 | 300 | 0.070686 | 70.6858 | 4241.1501 | 254469.0049 | 254.469 | 4.2412 | 0.070686 | 6.1073 | 38413.4867 | 52044.0823
| 350 | 350 | 0.096211 | 96.2113 | 5772.6765 | 346360.5901 | 346.3606 | 5.7727 | 0.096211 | 8.3127 | 52285.0236 | 70837.7787
| 400 | 400 | 0.12566 | 125.6637 | 7539.8224 | 452389.3421 | 452.3893 | 7.5398 | 0.12566 | 10.8573 | 68290.643 | 92522.813
| 500 | 500 | 0.19635 | 196.3495 | 11780.9725 | 706858.3471 | 706.8583 | 11.781 | 0.19635 | 16.9646 | 106704.1298 | 144566.8953
Standard (Code B) | General Purpose | PFA
High Grade (Code C) | Explosion Proof | Ceramic
Sanitary
AXG Integral or AXG4A | Submersible
AXFA11G
AXG1A
AXG Model | General Purpose | Ex | Sanitary | Submersible
2.5 | AXG002-G | AXG002-C | ERROR - INVALID TYPE | ERROR - INVALID TYPE
5 | AXG005-G | AXG005-C | ERROR - INVALID TYPE | ERROR - INVALID TYPE
10 | AXG010-G | AXG010-C | ERROR - INVALID TYPE | ERROR - INVALID TYPE
15 | AXG015-G | AXG015-C | AXG015-H | AXG015-W
25 | AXG025-G | AXG025-C | AXG025-H | AXG025-W
32 | AXG032-G | AXG032-C | AXG032-H | AXG032-W
40 | AXG040-G | AXG040-C | AXG040-H | AXG040-W
50 | AXG050-G | AXG050-C | AXG050-H | AXG050-W
65 | AXG065-G | AXG065-C | AXG065-H | AXG065-W
80 | AXG080-G | AXG080-C | AXG080-H | AXG080-W
100 | AXG100-G | AXG100-C | AXG100-H | AXG100-W
125 | AXG125-G | AXG125-C | AXG125-H | AXG125-W
150 | AXG150-G | AXG150-C | ERROR - INVALID TYPE | AXG150-W
200 | AXG200-G | AXG200-C | ERROR - INVALID TYPE | AXG200-W
250 | AXG250-G | AXG250-C | ERROR - INVALID TYPE | AXG250-W
300 | AXG300-G | AXG300-C | ERROR - INVALID TYPE | AXG300-W
350 | AXG350-G | AXG350-C | ERROR - INVALID TYPE | AXG350-W
400 | AXG400-G | AXG400-C | ERROR - INVALID TYPE | AXG400-W
500 | AXG500-G | ERROR - Not Available | ERROR - INVALID TYPE | AXG500-W
AXG Model
AXG032-G
AXG Model | Max Flow (m3/Hr)
2.5 | 0.1767
5 | 0.7068
10 | 2.8274
15 | 6.3617
25 | 17.6714
32 | 28.9529
40 | 45.2389
50 | 70.6858
65 | 119.459
80 | 180.955
100 | 282.743
125 | 441.786
150 | 636.172
200 | 1130.97
250 | 1767.14
300 | 2544.69
350 | 3463.6
400 | 4523.89
500 | 7068.58
Created By:
Simon Lillie
Yokogawa Australia Pty Ltd
June 2017
Rev 0 - July 2017 | ADMAG TI AXG Release
Rev 1 - Jan 2019
Rev 2 - Aug 2019 | AXG1A Release
Made by Yokogawa Australia Pty Ltd
Simon Lillie - 2019
Note on D8: AXG Liner: -PFA: Sizes 2.5 to 500mm -Ceramic: Sizes 2.5 to 200mm
Note on D9: Liner: -General Purpose: PFA or Ceramic -Explosion Proof: PFA or Ceramic -Sanitary: Only PFA available -Submersible: PFA or Ceramic
Note on D10: High Grade Calibration: -Only for Sizes 25 to 200mm
Note on C16: Based on PFA Liner only
Note on B18: Span Check: -Velocity >=0.1m/sec -Velocity <=10m/sec

## Sheet1
PAC
PAM
5mm

## AXG Accuracy Estimation
YOKOGAWA AXG MAGNETIC FLOWMETER - ACCURACY STATEMENT
Client:
Service:
Tag No:
Model: | AXG032-G
Type: | General Purpose
Liner: | PFA |  | FLOWRATE |  | ACCURACY
Excitation: | Dual Frequency |  | l/min | % of Range | % of Rate
Transmitter: | AXG Integral or AXG4A |  | 100 | 100 | 0.3
Size: | 32 | mm | 90 | 90 | 0.3
|  |  | 80 | 80 | 0.3
Rate Units | l/min |  | 70 | 70 | 0.3
FLOWRATE RANGE |  |  | 60 | 60 | 0.3
Range | 100 | l/min | 50 | 50 | 0.3
Zero | 0 |  | 40 | 40 | 0.3
|  |  | 30 | 30 | 0.3
VELOCITY RANGE |  |  | 20 | 20 | 0.3
Range | 2.0723 | m/sec | 10 | 10 | 0.3
Zero | 0 |  | 5 | 5 | 0.48255
MAXIMUM RANGE LIMITS |  |  | VELOCITY MAX RANGE LIMITS
Range | 482.5486 | l/min | Range | 10 | m/sec
Zero | 0 |  | Zero | 0

## AXG Calculator
|  |  | AXG | AXG | AXG | AXFA11 | AXFA11 | AXFA11 | AXFA11 | AXG1A | AXG1A | AXG1A | AXG1A
Span Vs | 2.0723 | m/sec | Size 2.5 to 15mm | Size 25 to 400mm |  | Size 2.5 to 15mm | Size 25 to 400mm |  | Size 500mm | Size 2.5 to 15mm | Size 25 to 400mm |  | Size 500mm
Size (mm) | 32 |  | PFA/Ceramic | PFA/Ceramic | PFA/Ceramic | PFA/Ceramic | PFA/Ceramic | PFA/Ceramic | PFA/Ceramic | PFA/Ceramic | PFA/Ceramic | PFA/Ceramic | PFA/Ceramic
|  |  | Standard (Code B) | Standard (Code B) | High Grade (Code C) | Standard (Code B) | Standard (Code B) | High Grade (Code C) | Standard (Code B) | Standard (Code B) | Standard (Code B) | High Grade (Code C) | Standard (Code B)
Liner | PFA | AXG Integral or AXG4A |  | TRUE | TRUE |  | TRUE | TRUE | FALSE |  | TRUE | TRUE | FALSE
Calibration | Standard (Code B) |  |  | TRUE | FALSE |  | FALSE | FALSE |  |  | FALSE | FALSE
|  |  | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | % of Span | % of Rate
% of Span | Velocity (m/sec) | Velocity (mm/sec)
100 | 2.0723 | 2072.33 | 0.3 | 0.3 | 0.15 | 0.35 | 0.35 | 0.2 | 0.39825 | 0.3 | 0.3 | 0.15 | 0.39825 | 100 | 0.3
97.5 | 2.0205 | 2020.5217 | 0.3 | 0.3 | 0.15 | 0.35 | 0.35 | 0.2 | 0.39949 | 0.3 | 0.3 | 0.15 | 0.39949 | 97.5 | 0.3
95 | 1.9687 | 1968.7135 | 0.3 | 0.3 | 0.15 | 0.35 | 0.35 | 0.2 | 0.40079 | 0.3 | 0.3 | 0.15 | 0.40079 | 95 | 0.3
92.5 | 1.9169 | 1916.9052 | 0.3 | 0.3 | 0.15 | 0.35 | 0.35 | 0.2 | 0.40217 | 0.3 | 0.3 | 0.15 | 0.40217 | 92.5 | 0.3
90 | 1.8651 | 1865.097 | 0.3 | 0.3 | 0.15 | 0.35 | 0.35 | 0.2 | 0.40362 | 0.3 | 0.3 | 0.15 | 0.40362 | 90 | 0.3
87.5 | 1.8133 | 1813.2887 | 0.3 | 0.3 | 0.15 | 0.35 | 0.35 | 0.2 | 0.40515 | 0.3 | 0.3 | 0.15 | 0.40515 | 87.5 | 0.3
85 | 1.7615 | 1761.4805 | 0.3 | 0.3 | 0.15 | 0.35 | 0.35 | 0.2 | 0.40677 | 0.3 | 0.3 | 0.15 | 0.40677 | 85 | 0.3
82.5 | 1.7097 | 1709.6722 | 0.3 | 0.3 | 0.15 | 0.35 | 0.35 | 0.2 | 0.40849 | 0.3 | 0.3 | 0.15 | 0.40849 | 82.5 | 0.3
80 | 1.6579 | 1657.864 | 0.3 | 0.3 | 0.15 | 0.35 | 0.35 | 0.2 | 0.41032 | 0.3 | 0.3 | 0.15 | 0.41032 | 80 | 0.3
77.5 | 1.6061 | 1606.0557 | 0.3 | 0.3 | 0.15 | 0.35 | 0.35 | 0.2 | 0.41226 | 0.3 | 0.3 | 0.15 | 0.41226 | 77.5 | 0.3
75 | 1.5542 | 1554.2475 | 0.3 | 0.3 | 0.15 | 0.35 | 0.35 | 0.2 | 0.41434 | 0.3 | 0.3 | 0.15 | 0.41434 | 75 | 0.3
72.5 | 1.5024 | 1502.4392 | 0.3 | 0.3 | 0.15 | 0.35 | 0.35 | 0.2 | 0.41656 | 0.3 | 0.3 | 0.15 | 0.41656 | 72.5 | 0.3
70 | 1.4506 | 1450.631 | 0.3 | 0.3 | 0.15 | 0.35 | 0.35 | 0.2 | 0.41894 | 0.3 | 0.3 | 0.15 | 0.41894 | 70 | 0.3
67.5 | 1.3988 | 1398.8227 | 0.3 | 0.3 | 0.15 | 0.35 | 0.35 | 0.2 | 0.42149 | 0.3 | 0.3 | 0.15 | 0.42149 | 67.5 | 0.3
65 | 1.347 | 1347.0145 | 0.3 | 0.3 | 0.15 | 0.35 | 0.35 | 0.2 | 0.42424 | 0.3 | 0.3 | 0.15 | 0.42424 | 65 | 0.3
62.5 | 1.2952 | 1295.2062 | 0.3 | 0.3 | 0.15 | 0.35 | 0.35 | 0.2 | 0.42721 | 0.3 | 0.3 | 0.15 | 0.42721 | 62.5 | 0.3
60 | 1.2434 | 1243.398 | 0.3 | 0.3 | 0.15 | 0.35 | 0.35 | 0.2 | 0.43042 | 0.3 | 0.3 | 0.15 | 0.43042 | 60 | 0.3
57.5 | 1.1916 | 1191.5897 | 0.3 | 0.3 | 0.15 | 0.35 | 0.35 | 0.2 | 0.43392 | 0.3 | 0.3 | 0.15 | 0.43392 | 57.5 | 0.3
55 | 1.1398 | 1139.7815 | 0.3 | 0.3 | 0.15 | 0.35 | 0.35 | 0.2 | 0.43774 | 0.3 | 0.3 | 0.15 | 0.43774 | 55 | 0.3
52.5 | 1.088 | 1087.9732 | 0.3 | 0.3 | 0.15 | 0.35 | 0.35 | 0.2 | 0.44191 | 0.3 | 0.3 | 0.15 | 0.44191 | 52.5 | 0.3
50 | 1.0362 | 1036.165 | 0.3 | 0.3 | 0.15 | 0.35 | 0.35 | 0.2 | 0.44651 | 0.3 | 0.3 | 0.15 | 0.44651 | 50 | 0.3
47.5 | 0.98436 | 984.3567 | 0.3 | 0.3 | 0.20032 | 0.35 | 0.35 | 0.20032 | 0.45159 | 0.3 | 0.3 | 0.20032 | 0.45159 | 47.5 | 0.3
45 | 0.93255 | 932.5485 | 0.3 | 0.3 | 0.20145 | 0.35 | 0.35 | 0.20145 | 0.45723 | 0.3 | 0.3 | 0.20145 | 0.45723 | 45 | 0.3
42.5 | 0.88074 | 880.7402 | 0.3 | 0.3 | 0.20271 | 0.35 | 0.35 | 0.20271 | 0.46354 | 0.3 | 0.3 | 0.20271 | 0.46354 | 42.5 | 0.3
40 | 0.82893 | 828.932 | 0.3 | 0.3 | 0.20413 | 0.35 | 0.35 | 0.20413 | 0.47064 | 0.3 | 0.3 | 0.20413 | 0.47064 | 40 | 0.3
37.5 | 0.77712 | 777.1237 | 0.3 | 0.3 | 0.20574 | 0.35 | 0.35 | 0.20574 | 0.47868 | 0.3 | 0.3 | 0.20574 | 0.47868 | 37.5 | 0.3
35 | 0.72532 | 725.3155 | 0.3 | 0.3 | 0.20757 | 0.35 | 0.35 | 0.20757 | 0.48787 | 0.3 | 0.3 | 0.20757 | 0.48787 | 35 | 0.3
32.5 | 0.67351 | 673.5072 | 0.3 | 0.3 | 0.2097 | 0.35 | 0.35 | 0.2097 | 0.49848 | 0.3 | 0.3 | 0.2097 | 0.49848 | 32.5 | 0.3
30 | 0.6217 | 621.699 | 0.3 | 0.3 | 0.21217 | 0.35 | 0.35 | 0.21217 | 0.51085 | 0.3 | 0.3 | 0.21217 | 0.51085 | 30 | 0.3
27.5 | 0.56989 | 569.8907 | 0.3 | 0.3 | 0.21509 | 0.35 | 0.35 | 0.21509 | 0.52547 | 0.3 | 0.3 | 0.21509 | 0.52547 | 27.5 | 0.3
25 | 0.51808 | 518.0825 | 0.3 | 0.3 | 0.2186 | 0.35 | 0.35 | 0.2186 | 0.54302 | 0.3 | 0.3 | 0.2186 | 0.54302 | 25 | 0.3
22.5 | 0.46627 | 466.2742 | 0.3 | 0.3 | 0.22289 | 0.35 | 0.35 | 0.22289 | 0.56447 | 0.3 | 0.3 | 0.22289 | 0.56447 | 22.5 | 0.3
20 | 0.41447 | 414.466 | 0.3 | 0.3 | 0.22825 | 0.35 | 0.35 | 0.22825 | 0.59127 | 0.3 | 0.3 | 0.22825 | 0.59127 | 20 | 0.3
17.5 | 0.36266 | 362.6577 | 0.3 | 0.3 | 0.23515 | 0.35 | 0.35 | 0.23515 | 0.62574 | 0.3 | 0.3 | 0.23515 | 0.62574 | 17.5 | 0.3
15 | 0.31085 | 310.8495 | 0.3 | 0.3 | 0.24434 | 0.35 | 0.35 | 0.24434 | 0.6717 | 0.3 | 0.3 | 0.24434 | 0.6717 | 15 | 0.3
12.5 | 0.25904 | 259.0412 | 0.38604 | 0.3 | 0.25721 | 0.38604 | 0.35 | 0.25721 | 0.77208 | 0.38604 | 0.3 | 0.25721 | 0.77208 | 12.5 | 0.3
10 | 0.20723 | 207.233 | 0.48255 | 0.3 | 0.27651 | 0.48255 | 0.35 | 0.27651 | 0.9651 | 0.48255 | 0.3 | 0.27651 | 0.9651 | 10 | 0.3
9 | 0.18651 | 186.5097 | 0.53617 | 0.3 | 0.28723 | 0.53617 | 0.35 | 0.28723 | 1.0723 | 0.53617 | 0.3 | 0.28723 | 1.0723 | 9 | 0.3
8 | 0.16579 | 165.7864 | 0.60319 | 0.3 | 0.30064 | 0.60319 | 0.35 | 0.30064 | 1.2064 | 0.60319 | 0.3 | 0.30064 | 1.2064 | 8 | 0.3
7 | 0.14506 | 145.0631 | 0.68936 | 0.34468 | 0.34468 | 0.68936 | 0.34468 | 0.34468 | 1.3787 | 0.68936 | 0.34468 | 0.34468 | 1.3787 | 7 | 0.34468
6 | 0.12434 | 124.3398 | 0.80425 | 0.40212 | 0.40212 | 0.80425 | 0.40212 | 0.40212 | 1.6085 | 0.80425 | 0.40212 | 0.40212 | 1.6085 | 6 | 0.40212
5 | 0.10362 | 103.6165 | 0.9651 | 0.48255 | 0.48255 | 0.9651 | 0.48255 | 0.48255 | 1.9302 | 0.9651 | 0.48255 | 0.48255 | 1.9302 | 5 | 0.48255
4 | 0.082893 | 82.8932 | 1.2064 | 0.60319 | 0.60319 | 1.2064 | 0.60319 | 0.60319 | 2.4127 | 1.2064 | 0.60319 | 0.60319 | 2.4127 | 4 | 0.60319
3 | 0.06217 | 62.1699 | 1.6085 | 0.80425 | 0.80425 | 1.6085 | 0.80425 | 0.80425 | 3.217 | 1.6085 | 0.80425 | 0.80425 | 3.217 | 3 | 0.80425
2 | 0.041447 | 41.4466 | 2.4127 | 1.2064 | 1.2064 | 2.4127 | 1.2064 | 1.2064 | 4.8255 | 2.4127 | 1.2064 | 1.2064 | 4.8255 | 2 | 1.2064
1 | 0.020723 | 20.7233 | 4.8255 | 2.4127 | 2.4127 | 4.8255 | 2.4127 | 2.4127 | 9.651 | 4.8255 | 2.4127 | 2.4127 | 9.651 | 1 | 2.4127